Software Change Document

Model Number: S-3400		Product Name: IPSCOM(Software)

Date: 11/02/23				Name: Shashank Kanna

Release Type:		 Initial	 Maintenance	 Special Request

Software Version: D-0345V10.16.01

| Attachments Included: |  |  |  |
| --- | --- | --- | --- |
| Document Name | Yes | No | Not Applicable |
| Specifications |  |  |  |
| Schematics |  |  |  |
| Assembly Drawings |  |  |  |
| Software Description |  |  |  |
| Special Instructions |  |  |  |
| Support Software |  |  |  |

Software Control Checklist

___SK___ (ETL) -  Design Review Complete Assure software meets requirements of design input

___SK___ (ETL) -  New software assigned a unique number

___SK___ (ETL/SE) -  Archive and distribute software for testing

___CL___ (ELS) -  Develop software verification test plan

___CL___ (ELS) -  Perform testing per plan

___CL___ (ELS) -  Authorize software release to QA for validation testing

Changes Made:

| Tracker | Subject | Severity |
| --- | --- | --- |
| 16581 | DTL 90: IPSlogic dropout does not record in SOE or it is recorded but it is named "Timeout" | 3- Medium (No Workaround) |
| 16579 | DTL 65: S-3400 IPScom for older relays (M-3420, M-3430) does not display correct setting ranges for some settings for 1A relays | 3- Medium (No Workaround) |
| 16578 | DTL 48: S-3400 IPScom 87 characteristic monitoring screens plot 87 2nd slope at values above 150% even though code limits it to 150%. | 3- Medium (No Workaround) |
| 16577 | DTL 34: Using the S-3400 IPScom it is not currently possible to select “IN” for the Operating Current in the 67N settings for an M-3425A relay when creating an off-line relay setting file | 3- Medium (No Workaround) |
| 16606 | Display IO Map: Unhandled Issue while Enabling TC Function | 3- Medium (No Workaround) |
| 16353 | File Compare | 3- Medium (No Workaround) |
| 16352 | File Compare | 3- Medium (No Workaround) |

Glossary:

ETL – Engineering Team Leader

SE – Software Engineer

ELS – Engineering Lab Supervisor

VTE – Validation Test Engineer

VTSE – Validation Test Software Engineer